## Sheet1
NO. | PAGE | Before | After | 说明 | Note
1 | Indoor Wire Diagram |  |  | 此处接线需根据现场实际情况（单冷/冷暖/1级压缩/2级压缩）进行接线，删除有歧义的接线图示，请参考说明书中详细的接线方式。 | The wiring here needs to be done according to the actual situation on site (single cooling/cold and warm/1-stage compression/2-stage compression). Delete the ambiguous wiring diagram. Please refer to the detailed wiring method in the manual.
2 | Outdoor Wire Diagram |  |  | 此处接线需根据现场实际情况（单冷/冷暖/1级压缩/2级压缩）进行接线，删除有歧义的接线图示，请参考说明书中详细的接线方式。 | The wiring here needs to be done according to the actual situation on site (single cooling/cold and warm/1-stage compression/2-stage compression). Delete the ambiguous wiring diagram. Please refer to the detailed wiring method in the manual.
1 | P27 |  |  | 双级热泵，化霜信号D端子接入内机W1，可在机组化霜时打开电加热。 | Two-stage heat pump, the defrost signal D terminal is connected to the indoor unit W1, and the electric heating can be turned on when the unit is defrosted.
2 | P27 |  |  | 双级单冷，取消R的接线。 | Two-stage single cooling, cancel the wiring of R.
3 | P27 |  |  | 单级热泵，化霜信号D端子接入内机W1，可在机组化霜时打开电加热。 | Single-stage heat pump, the defrost signal D terminal is connected to the indoor unit W1, and the electric heating can be turned on when the unit is defrosted.
4 | P27 |  |  | 单级单冷，取消R的接线。 | Single-stage single cooling, cancel the wiring of R.